## Slide 1: Dampak FAÇADES pada Efisiensi Energi Bangunan

## Slide 2
Konsumsi Energi A.S. menurut Sektor. Reorganisasi data yang ada menggabungkan energi yang dibutuhkan untuk menjalankan bangunan perumahan, komersial, dan industri bersama dengan energi yang terkandung dari bahan-bahan yang dihasilkan industri seperti karpet, ubin, dan perangkat keras - memaparkan arsitektur sebagai pencemar tersembunyi
Source : Architecture 2030
architecture is the hidden polluter

## Slide 3
What shall we do?
DESIGN STRATEGIES
TECHNOLOGIES AND SYSTEMS
OFF-SITE RENEWABLE ENERGY

## Slide 4
Source : UK Energy Efficiency Best Practice Program Energy Consumption Guide 19: Energy Use in Offices
ENERGY USE IN OFFICES

## Slide 5
Beban AC disebabkan oleh pencahayaan, peralatan, orang-orang dan panas yang diperoleh melalui fasad

## Slide 6
Seberapa efisien façade Anda?

## Slide 7: OTTV Overall Thermal Transfer Value
WATTS PER M2

## Slide 8
HEAT W =
OTTV x skin area
W / m2 x m2

## Slide 9
external
environment

## Slide 10
OTTV
x (1-WWR) x Uw + x WWR x Uf + x x WWR x
CF
Tdeq
SC
SF
DT
DIFFERENTIAL TEMPERATURE EQUIVALENT
TEMPERATURE DIFFERENCE
SOLAR FACTOR
SOLAR CORRECTION FACTOR
SHADING COEFFICIENT

## Slide 11
α (1 −WWR)Uw + (WWR)Uf + ( x CF x WWR x SC)
15
6
194
OTTV Simplified Formula

## Slide 12
Qgc
glass conduction
Qwc
wall conduction
Qgs
glass
solar

## Slide 13
α (1 −WWR)Uw + (WWR)Uf + ( x CF x WWR x SC)
15
6
194
WALL HEAT
WINDOW HEAT
SOLAR THROUGH GLASS
OTTV

## Slide 14
Qgc
glass conduction
Qwc
wall conduction
Qgs
glass
solar
5%
10% - 20%
80%

## Slide 15
15 (1 −WWR) + 6(WWR) + (194 x x WWR x )
OTTV
Simplified Formula
α
Uw Uf
SC
CF
BLACK | 0.9 – 1.0
WHITE | 0.15 – 0.3
SILVER / ALUMINIUM | 0.1
SOLAR ABSORPTION FACTOR
U VALUE

## Slide 16
15 (1 −WWR) + 6(WWR) + (194 x x WWR x )
OTTV
α
Uw Uf
SC
CF
SOLAR CORRECTION FACTOR

## Slide 17
Orientation of Buildings

## Slide 18
15 (1 −WWR) + 6(WWR) + (194 x x WWR x )
OTTV
α
Uw Uf
SC
CF
SHADING COEFFICIENT

## Slide 19
The lower the SC, the darker the interior

## Slide 20
The higher the VLT, the lighter the interior,
but beware of GLARE

## Slide 21
SHADING
COEFFICIENT
SC
SC = SC1 x SC2

## Slide 23
15 (1 − ) + 6( ) + (194 x x x )
OTTV
α
Uw Uf
SC
CF
Window Wall Ratio
WWR WWR WWR

## Slide 24
The Window Wall Ratio

## Slide 25
Window Wall
Ratio

## Slide 26
 | WWR - Window / Wall Ratio (%) |  |  |  |  |  |  |  |  | 
 | 11 | 13 | 15 | 17 | 19 | 21 | 23 | 25 | 27 | 29
OTTV | 36 | 39 | 44 | 47 | 51 | 55 | 59 | 63 | 67 | 71

## Slide 28
Sound insulation does not work when the air gap is small, say 6 mm
Increase air gap = 20 - 100 mm
DGU
double glazed unit

## Slide 29
Low-Emissivity Glass
Type of Glass | R Value
Single Pane regular glass | 0.85
Clear Insulated Glass 7/8 inch overall thickness | 2.08
Hard Coat Low-E insulated glass | 2.45
Hard Coat Low-E insulated glass with argon | 2.75
Soft Coat Low-E insulated Glass | 3.50
Soft Coat Low-E insulated glass with argon | 4.35

## Slide 30
Soft Coat Low-E glass
Silver, zinc, or tin are sputtered onto the surface of the glass where they stick. Coating is not strong and easily scratched
Hard Coat Low-E glass
Molten tin is heat welded to the glass. Coating is very strong and difficult to scratch or remove

## Slide 31: THANK YOU
Fenestra Malaysia Sdn Bhd
J-5-12 Solaris Mont Kiara
2 Jalan Solaris
50480 Kuala Lumpur
T +603 6205 1288
F +603 6205 1289
E info@fenestra.com.my